BUCKMAN DIGITAL WATER

Monthly Cooling Water Performance Report

Candler Hospital Savannah GA (US)

Reporting Month: August 2026

| Customer / Site | System | Controller | Prepared For |
| --- | --- | --- | --- |
| Candler Hospital Savannah GA (US) | Cooling Tower | 84253FAB8C75 | Monthly Performance Review |

This report summarises corrosion control, scale control, microbial control, water efficiency, product efficiency, and proactive system support for Candler Hospital Savannah GA (US), August 2026, using controller setpoints, telemetry KPIs, field data, and service note records.

| Prepared By | Prepared Date | Report Status |
| --- | --- | --- |
| Buckman Digital Water | 21 September 2026 | Draft |

Executive Summary

System Health Check

Corrosion Control

Status: Excellent

During the reporting period, the system remained under good control. The mild steel and copper corrosion rates averaged 0.51 mpy and 0.11 mpy, respectively, both of which are well within the recommended limits of <5 mpy and <0.5 mpy.

Scale Control

Status: Acceptable

Traced Product was within the recommended range for 41.8% of the reporting month. Polymer consumption rate averaged 50.7% and increased from 48.2% at the start of the month to 53.9% at the end of the month. Conductivity was within the recommended range for 10.1% of the reporting month. End-of-month Traced Product was 6.1% higher than the setpoint, and conductivity was also not maintained, so the product trend should be treated as conductivity-related until cycles, blowdown, makeup, or dilution behavior is corrected. Conductivity was below its setpoint configuration range for most of the same period, so water loss, dilution, or blowdown/makeup behavior should be inspected during the upcoming service visit. Because polymer consumption increased by more than 5%, phosphate residual will be checked during the upcoming service visit.

Microbial Control

Status: Acceptable

Insufficient ORP spike was observed during oxidizing biocide application, so oxidizing biocide feed response should be reviewed during the upcoming service visit. FRC and dip-slide will be analysed in the upcoming visit to ensure good microbial control.

Water Efficiency

Status: Acceptable

| MU Conductivity | Target COC | Actual COC | Deviation | Status |
| --- | --- | --- | --- | --- |
| 300.0 µS/cm | 2.0 | 1.59 | 20.4% | Acceptable |

| System | Current COC | Target COC | Decrease | Annual Water Loss | Estimated Cost |
| --- | --- | --- | --- | --- | --- |
| Candler Hospital_ACM | 1.59 | 2.00 | 20.5% | 2,561,298 gal/year | $128,064.89/year |

Because current COC is more than 20% below the value-creation Target COC, estimated avoidable makeup water is 2,561,298 gallons per annum. At a makeup water cost of $5 per 100 gallons, the estimated annual savings opportunity is $128,064.89.

Water efficiency was Critical. Conductivity averaged 477.35 uS/cm against the 570.00-630.00 uS/cm Controller Setpoint range, with only 10.1% of readings in range. Conductivity increased from about 381.2 uS/cm early in the month to 573.4 uS/cm later, but the monthly average remained below the configured range. Dilution, water loss, excess blowdown, or makeup changes should be reviewed.

Product Efficiency

Status: Acceptable

Product efficiency needs attention because Traced Product averaged 73.90 ppm against the 70.00 ppm setpoint and the 67.00-73.00 ppm control range. Because conductivity was also not maintained, product control should be reviewed together with cycles, blowdown, makeup, and dilution behavior before changing feed settings.

Proactive System Support

No service notes were recorded for the August reporting period. Recommended follow-up: Confirm inhibitor residual, inspect for deposit activity, and compare corrosion movement with ORP and product trends. Traced Product was not maintained while conductivity was also not maintained, so treat the product issue as conductivity-related and check cycles, blowdown, makeup, and dilution behavior first. Review makeup conductivity and blowdown control because cycles of concentration are still deviating from target. Check FRC during the upcoming service visit to confirm oxidizing biocide residual. Measure dip-slide CFU during the upcoming service visit to confirm microbial control. Verify phosphate and silica residuals during the next service visit.

Performance Summary

Controller Setpoints are used as control limits below. % In Range is calculated from the full reporting month telemetry.

| Parameter | Context Point | Average | Std Dev | Min | Max | Lower Limit | Upper Limit | % In Range | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Corrosion – MS (MPY) | ACM Skid | 0.514 | 0.105 | 0.161 | 0.895 | 0.00 | 3.00 | 100.0% | ✓ Excellent |
| Corrosion – Cu (MPY) | ACM Skid | 0.114 | 0.058 | 0.017 | 0.260 | 0.00 | 0.50 | 100.0% | ✓ Excellent |
| Traced Product (ppm) | ACM Skid | 73.896 | 4.547 | 66.258 | 85.742 | 67.0 | 73.0 | 41.8% | ⚠ Acceptable |
| Conductivity (µS/cm) | ACM Skid | 477.351 | 143.214 | 316.970 | 912.920 | 570 | 630 | 10.1% | ✗ Critical |
| pH | ACM Skid | 8.648 | 0.080 | 8.403 | 8.842 | 7.50 | 10.00 | 100.0% | ℹ Info |
| ORP (mV) | ACM Skid | 144.914 | 18.604 | 108.154 | 185.521 | – | – | – | See chart |
| Turbidity (NTU) | ACM Skid | 0.044 | 0.147 | 0.000 | 3.984 | – | 75.0 | – | ℹ Info |
| Cell Fouling (%) | ACM Skid | 0.001 | 0.028 | 0.000 | 1.019 | – | 30.0 | – | ℹ Info |
| FRC | Field Data | Not avail. | – | – | – | – | – | – | ⚠ Check |

Charts and Comments

Corrosion Rate

Figure 1: Corrosion Rate — August 2026

Comment: Pattern: corrosion control is increasing, but remains good against the target.
Mild steel corrosion increased across the month, while copper corrosion increased across the month.
MS was within the 3.0 MPY target, and Cu was within the 0.5 MPY target.
Likely reason: corrosion is still protected, but increasing movement should be checked against product and ORP trends.

Traced Product Control Trend

Figure 2: Traced Product — August 2026

Comment: Pattern: Traced Product is still not maintained at the end of the month.
The trend moved from about 73.3 ppm at the start to 74.5 ppm at the end.
The Traced Product average was above the configured range. The monthly in-range performance was 41.8%.
Likely reason: Traced Product is following the increased conductivity trend, so cycles, blowdown, makeup, or dilution changes should be corrected first.

ORP vs Copper Corrosion Rate

Figure 3: ORP vs Copper Corrosion Rate — August 2026

Comment: Pattern: ORP response is decreasing across the month.
ORP did not show a strong spike response pattern during the month without relying on absolute ORP values.
Copper corrosion increased across the month while the ORP pattern changed.
Likely reason: biocide feed timing, relay operation, oxidizer inventory, or field FRC residual should be checked.

Oxidizing Biocide Pump Relay vs Copper Corrosion

Figure 4: Oxidizing Biocide Pump Relay vs Copper Corrosion — August 2026

Comment: Pattern: biocide feed versus copper corrosion is increasing, but remains good against the target.
Biocide relay activity was present in the monthly trend.
Relay activity increased across the month when the month is split into early and late periods.
Likely reason: relay feed timing is adequate and copper corrosion remains protected.

Electrode Conductivity

Figure 5: Electrode Conductivity — August 2026

Comment: Pattern: conductivity is increasing and needs attention against the target.
The trend moved from about 381.2 µS/cm at the start to 573.4 µS/cm at the end.
The conductivity average was below the configured range. The monthly in-range performance was 10.1%.
Likely reason: dilution, water loss, excess blowdown, or makeup changes are keeping conductivity low.

Closing Summary

Overall August performance for Candler main showed Excellent corrosion control and Acceptable microbial control, while conductivity and Traced Product control require follow-up. The primary action is to stabilize conductivity first because the Traced Product deviation is linked with conductivity behavior. After water-side control is stabilized, product residual and polymer efficiency should be verified during the next service visit.