BUCKMAN DIGITAL WATER

Monthly Cooling Water Performance Report

Flowserve US Raleigh NC (US)

Reporting Month: August 2026

| Customer / Site | System | Controller | Prepared For |
| --- | --- | --- | --- |
| Flowserve US Raleigh NC (US) | Cooling Tower | 84253F5EE1C9 | Monthly Performance Review |

This report summarises corrosion control, scale control, microbial control, water efficiency, product efficiency, and proactive system support for Flowserve US Raleigh NC (US), August 2026, using controller setpoints, telemetry KPIs, field data, and service note records.

| Prepared By | Prepared Date | Report Status |
| --- | --- | --- |
| Buckman Digital Water | 08 September 2026 | Draft |

Executive Summary

System Health Check

Corrosion Control

Status: Excellent

The average mild steel corrosion rate was 0.61 MPY against the target of within 3.0 MPY, and the average copper corrosion rate was 0.02 MPY against the target of within 0.5 MPY.

Scale Control

Status: Acceptable

Traced Product was within the Controller Setpoint control range for 29.9% of the reporting month. Polymer consumption rate averaged 62.5% and increased from 60.2% at the start of the month to 65.6% at the end of the month. Conductivity was within the Controller Setpoint control range for 13.2% of the reporting month. End-of-month Traced Product was 7.0% higher than the setpoint, and conductivity was also not maintained, so the product trend should be treated as conductivity-related until cycles, blowdown, makeup, or dilution behavior is corrected. Conductivity was below its setpoint configuration range for most of the same period, so water loss, dilution, or blowdown/makeup behavior should be inspected during the upcoming service visit. Because polymer consumption increased by more than 5%, phosphate residual will be checked during the upcoming service visit.

Microbial Control

Status: Acceptable

FRC data was not available in the field data for this reporting period and will be checked during the upcoming service visit. ORP did not show a strong spike response pattern during the month, but biocide relay activity was present, supporting an Acceptable microbial control status pending field residual confirmation. Copper corrosion remained within target, indicating no copper corrosion upset was observed during the reporting period.

Dip-slide analysis was not available for this reporting period and will be measured during the upcoming service visit.

Water Efficiency

Makeup water conductivity is not available for this site. Actual cycles of concentration cannot be calculated. Makeup conductivity should be captured at the next service visit.

Water efficiency was Critical. Conductivity averaged 891.67 uS/cm against the 930.00-970.00 uS/cm Controller Setpoint range, with only 13.2% of readings in range. Conductivity stayed below the configured range and moved slightly from about 889.4 uS/cm early to 893.9 uS/cm later in the month. Makeup conductivity was not available, so actual cycles of concentration could not be calculated; dilution, water loss, excess blowdown, or makeup changes should be reviewed.

Product Efficiency

Status: Acceptable

Product efficiency needs attention because Traced Product averaged 90.26 ppm against the 85.00 ppm setpoint and the 82.00-88.00 ppm control range, with only 29.9% of readings in range. Because conductivity was also not maintained, product-control review should first be tied to conductivity, blowdown, makeup, dilution, or water-loss behavior before changing feed settings.

Proactive System Support

No service notes were recorded for the August reporting period. Recommended follow-up: Confirm inhibitor residual, inspect for deposit activity, and compare corrosion movement with ORP and product trends. Traced Product was not maintained while conductivity was also not maintained, so treat the product issue as conductivity-related and check cycles, blowdown, makeup, and dilution behavior first. Capture makeup water conductivity during the next service visit so actual cycles of concentration can be verified. Check FRC during the upcoming service visit to confirm oxidizing biocide residual. Measure dip-slide CFU during the upcoming service visit to confirm microbial control. Verify phosphate and silica residuals during the next service visit.

Performance Summary

Controller Setpoints are used as control limits below. % In Range is calculated from the full reporting month telemetry.

| Parameter | Context Point | Average | Std Dev | Min | Max | Lower Limit | Upper Limit | % In Range | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Corrosion – MS (MPY) | ACM Skid | 0.612 | 0.220 | 0.249 | 1.924 | 0.00 | 3.00 | 100.0% | ✓ Excellent |
| Corrosion – Cu (MPY) | ACM Skid | 0.020 | 0.010 | 0.000 | 0.092 | 0.00 | 0.50 | 100.0% | ✓ Excellent |
| Traced Product (ppm) | ACM Skid | 90.262 | 8.982 | 75.095 | 303.263 | 82.0 | 88.0 | 29.9% | ⚠ Acceptable |
| Conductivity (µS/cm) | ACM Skid | 891.668 | 36.697 | 570.220 | 967.757 | 930 | 970 | 13.2% | ✗ Critical |
| pH | ACM Skid | 8.835 | 0.151 | 8.412 | 9.055 | 7.50 | 10.00 | 100.0% | ℹ Info |
| ORP (mV) | ACM Skid | 525.698 | 106.369 | 59.013 | 715.000 | – | – | – | See chart |
| Turbidity (NTU) | ACM Skid | 5.754 | 0.592 | 3.150 | 6.947 | – | 75.0 | – | ℹ Info |
| Cell Fouling (%) | ACM Skid | 20.467 | 2.009 | 17.086 | 25.674 | – | 30.0 | – | ℹ Info |
| FRC | Field Data | Not avail. | – | – | – | – | – | – | ⚠ Check |

Charts and Comments

Corrosion Rate

Figure 1: Corrosion Rate — August 2026

Comment: Pattern: corrosion control is increasing, but remains good against the target.
Mild steel corrosion increased across the month, while copper corrosion decreased across the month.
MS was within the 3.0 MPY target, and Cu was within the 0.5 MPY target.
Likely reason: corrosion is still protected, but increasing movement should be checked against product and ORP trends.

Traced Product Control Trend

Figure 2: Traced Product — August 2026

Comment: Pattern: Traced Product is still not maintained at the end of the month.
The trend moved from about 89.6 ppm at the start to 90.9 ppm at the end.
The Traced Product average was above the configured range. The monthly in-range performance was 29.9%.
Likely reason: conductivity was not maintained, so the Traced Product variation should be tied to conductivity control before assigning another cause.

ORP vs Copper Corrosion Rate

Figure 3: ORP vs Copper Corrosion Rate — August 2026

Comment: Pattern: ORP response is decreasing across the month.
ORP did not show a strong spike response pattern during the month without relying on absolute ORP values.
Copper corrosion decreased across the month while the ORP pattern changed.
Likely reason: biocide feed timing, relay operation, oxidizer inventory, or field FRC residual should be checked.

Oxidizing Biocide Pump Relay vs Copper Corrosion

Figure 4: Oxidizing Biocide Pump Relay vs Copper Corrosion — August 2026

Comment: Pattern: biocide feed versus copper corrosion is decreasing, but remains good against the target.
Biocide relay activity was present in the monthly trend.
Relay activity increased across the month when the month is split into early and late periods.
Likely reason: relay feed timing is adequate and copper corrosion remains protected.

Electrode Conductivity

Figure 5: Electrode Conductivity — August 2026

Comment: Pattern: conductivity is stable and needs attention against the target.
The trend moved from about 889.4 µS/cm at the start to 893.9 µS/cm at the end.
The conductivity average was below the configured range. The monthly in-range performance was 13.2%.
Likely reason: dilution, water loss, excess blowdown, or makeup changes are keeping conductivity low.

Closing Summary

Overall August performance for Flowserve showed Excellent corrosion control and Acceptable microbial control, while water efficiency and Traced Product consistency need follow-up. The primary action is to investigate low conductivity and possible dilution, excess blowdown, makeup change, or water loss, then confirm product residual response after conductivity control is stabilized.