BUCKMAN DIGITAL WATER

Monthly Cooling Water Performance Report

Flowserve US Raleigh NC (US)

Reporting Month: July 2026

| Customer / Site | System | Controller | Prepared For |
| --- | --- | --- | --- |
| Flowserve US Raleigh NC (US) | Cooling Tower | 84253F5EE1C9 | Monthly Performance Review |

This report summarises corrosion control, scale control, microbial control, water efficiency, product efficiency, and proactive system support for Flowserve US Raleigh NC (US), July 2026, using controller setpoints, telemetry KPIs, field data, and service note records.

| Prepared By | Prepared Date | Report Status |
| --- | --- | --- |
| Buckman Digital Water | 12 August 2026 | Draft |

Executive Summary

System Health Check

Corrosion Control

Status: Excellent

The average mild steel corrosion rate was 1.10 MPY against the target of within 3.0 MPY, and the average copper corrosion rate was 0.0250 MPY against the target of within 0.5 MPY. Both corrosion indicators were maintained within the required control targets for the July reporting period, supporting excellent asset preservation for the cooling water system.

Scale Control

Status: Acceptable

Traced Product was within the Controller Setpoint control range for 41.3% of the reporting month. Polymer consumption rate averaged 64.3% and decreased from 64.6% at the start of the month to 64.3% at the end of the month. The product was higher than target during the initial part of the month and moved closer to the control band later, but end-of-month control was 52.4% within range, so it is not yet consistently maintained well. The end-of-month traced product deviation from setpoint is minimal, so the control logic will be optimised. Conductivity was below its setpoint configuration range for most of the same period, so water loss, dilution, or blowdown/makeup behavior should be inspected during the upcoming service visit.

Microbial Control

Status: Acceptable

FRC data was not available in the MDE data for this reporting period and will be checked during the upcoming service visit. ORP spike response after biocide feed was consistent, indicating the slug dosage of biocide is successful.

Dip-slide analysis was not available for this reporting period and will be measured during the upcoming service visit.

Water Efficiency

Makeup water conductivity is not available for this site. Actual cycles of concentration cannot be calculated. Makeup conductivity should be captured at the next service visit.

Conductivity averaged 890.6 uS/cm against the SCC range of 930-970 uS/cm, with 20.2% of July readings maintained within range. Makeup conductivity was not available, so current COC and target COC could not be calculated; this will be reviewed when makeup conductivity data is available. Because conductivity was below the control range for much of the period, possible water loss, makeup/blowdown behavior, or dilution should be inspected during the upcoming service visit.

Product Efficiency

Status: Acceptable

Traced Product was 41.3% within the SCC control range, and actual product consumption data was not available for direct comparison with target consumption. Product efficiency should be reviewed by checking calibration, feed settings, and pump operation, then comparing actual consumption once usage data is available.

Proactive System Support

No service notes were recorded for this reporting period. The main proactive follow-up items are to verify Traced Product feed and fluorometer calibration, review conductivity control and water balance, and collect FRC during the next service visit.

Performance Summary

Controller Setpoints are used as control limits below. % In Range is calculated from the full reporting month telemetry.

| Parameter | Context Point | Average | Std Dev | Min | Max | Lower Limit | Upper Limit | % In Range | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Corrosion – MS (MPY) | ACM Skid | 1.102 | 0.688 | 0.247 | 2.818 | 0.00 | 3.00 | 100.0% | ✓ Excellent |
| Corrosion – Cu (MPY) | ACM Skid | 0.025 | 0.143 | 0.010 | 3.308 | 0.00 | 0.50 | 99.8% | ✓ Excellent |
| Traced Product (ppm) | ACM Skid | 91.921 | 10.177 | 78.792 | 274.838 | 82.0 | 88.0 | 41.3% | ⚠ Acceptable |
| Conductivity (µS/cm) | ACM Skid | 890.606 | 44.201 | 453.220 | 988.564 | 930 | 970 | 20.2% | ✗ Critical |
| pH | ACM Skid | 8.455 | 0.256 | 7.458 | 8.914 | 7.50 | 10.00 | 100.0% | ℹ Info |
| ORP (mV) | ACM Skid | 549.451 | 152.851 | 78.917 | 819.747 | – | – | – | See chart |
| Turbidity (NTU) | ACM Skid | 3.160 | 1.191 | 1.643 | 38.197 | – | 75.0 | – | ℹ Info |
| Cell Fouling (%) | ACM Skid | 15.129 | 3.677 | 10.370 | 23.008 | – | 30.0 | – | ℹ Info |
| FRC | Field Data | Not avail. | – | – | – | – | – | – | ⚠ Check |

Charts and Comments

Corrosion Rate

Figure 1: Corrosion Rate — July 2026

Comment: Mild steel corrosion decreased across the month, while copper corrosion decreased across the month.
The monthly averages were MS 1.102 MPY and Cu 0.025 MPY when data was available.
MS was within the 3.0 MPY target, and Cu was within the 0.5 MPY target.
The pattern should continue to be monitored for any sustained upward corrosion movement.

Traced Product Control Trend

Figure 2: Traced Product — July 2026

Comment: Traced Product decreased across the month.
The trend moved from about 92.9 ppm at the start to 90.9 ppm at the end.
The Traced Product average was above the configured range. The monthly in-range performance was 41.3%.
This pattern indicates whether feed control is settling into the setpoint band or needs field review.

ORP vs Copper Corrosion Rate

Figure 3: ORP vs Copper Corrosion Rate — July 2026

Comment: ORP showed a visible spike response pattern during the month.
The ORP pattern increased across the month without using absolute ORP values.
Copper corrosion decreased across the month while the ORP pattern changed.
This pattern helps confirm whether biocide response is consistent without creating a corrosion upset.

Oxidizing Biocide Pump Relay vs Copper Corrosion

Figure 4: Oxidizing Biocide Pump Relay vs Copper Corrosion — July 2026

Comment: Biocide relay activity was present in the monthly trend.
Relay activity increased across the month when the month is split into early and late periods.
Copper corrosion decreased across the month during the same period.
The pattern should be reviewed with service observations to confirm feed timing and corrosion stability.

Electrode Conductivity

Figure 5: Electrode Conductivity — July 2026

Comment: Conductivity decreased across the month.
The trend moved from about 896.8 uS/cm at the start to 884.5 uS/cm at the end.
The conductivity average was below the configured range. The monthly in-range performance was 20.2%.
This pattern indicates whether cycles, makeup, blowdown, or dilution behavior needs follow-up.

Closing Summary

Flowserve US Raleigh NC maintained good corrosion control during July 2026, while scale control and product efficiency should continue to be reviewed because Traced Product was above the SCC range for part of the month. Conductivity control requires attention due to low in-range performance, and FRC should be measured during the upcoming service visit to confirm microbial control.