## Sheet1
Report Automation
1 | 1 st page- title
2 | 2 nd -3 rd page Executive summary
3 | Under Executive summary
4 | Corrosion control as 1 st heading
5 | Mention corrosion control status
6 | Calculate the avg MS and copper corrosion values
7 | Check if it's less than 3 mpy for MS corrosion rate
8 | Check if it's less than 0.5 mpy for Cu corrosion rate
9 | Mention whether how much % of time it's maintained within range
10 | Check whether 95% of time the corrosion is well mainatined within the range for copper and MS. If it's within range , mention it's well mainatined within the required range.
11 | If the corrosion rate is mainatined above the mentioned range in initial 10 days and later it has showed decreasing trend . Currently , if the value is within range. Run the particular alarm logic in back end and mention the reason. Also highlight rightnow, the situation is corrected and maintained in range.
12 | If the corrosion rate is mainatined above the mentioned range in last 10 days and if it has showed increasing trend of corrosion rate after a date. Mention that from which date it has showed incraesing date . Currently , if the value still remains high . Run the particular alarm logic in back end and mention the reason. If the value has started decreasing at point. Highlight this if it has started decreasing.
13 | Check if the pH has decreased and corrosion has incraesed, then mention as process leak in the system. Highlight once the
14 | Scale control as 2 nd heading
15 | Mention whether 100 % of time trace is maintained within range
16 | Mention scale control status
17 | If the trace is decreased, check whether cond is less. Then mention as water loss and will be inspected in upcoming service
18 | If the trace is decreased, check whether cond is maintained in range. Then mention that this could be due to lack of inventory/ dosing pump lost prime/ leak in the pump discharge line will be inspected in upcoming service
19 | If trace is higher than tag in almost 90% of time .Calculate the polymer consumption rate( trace- tag/trace) for each data point. Check if this value increased in the month. If so, say the scale control needs attention, check whether the ADE phosphate and silica residual entered on / after the date the increasing trend of polymer consumption is noticed. If ADE of phosphate and silica is not available, mention it will be measure in the upcoming service visit.
20 | Check whether pH has increased at any point of time, then also mention scale control needs attention, phosphate and silica residual will be checked in upcoming service visit.
21 | Check whether conductivity has increased and polymer consumption also increased. If yes, mention this is due to increase in Cycles of concentration.
22 | Microbial control as 3 rd heading
23 | Mention is the microbial control status
24 | Check the biocide dosage is intimer or on/off control .Mention that control type.
25 | If this in timer control/ delta timer, See if there is spikes in ORP reading. If not, insist that inventory level, functionality of dosing pump/ leak in pump discharge line will be checked.
26 | If the biocide control is in on/off. Check if it's within control. If not, mention that inventory level, functionality of dosing pump/ leak in pump discharge line will be checked.
27 | Take FRC level from ADE excel
28 | Mention whether FRC level is within range of 02-0.5 ppm.
29 | If it's below range, mention to increase biocide dosage. If the range is high, then mention that the biocide dosage will be reduced .
30 | If FRC level is not mentioned,Mention it will be measured in upcoming service visit
31 | If dip slide is not present, mention it will be measured in upcoming visit
32 | If there is dipslide analysis, mention corresponding cfu. If it is < 10^4 then its is in good microbial control.If it is < 10^2 then it i in excellent control. If the cfu is between 10^4 and 10^6 , then it needs attention. If cfu is <10^6 then it is critical and slug dosage duration needs to be increased.
33 | Water efficiency as 4 th heading
34 | Take only avg conductovity value diviode it by makeup conductivity and say the current COC.
35 | Take the setpoint divided by makeup conductivity and say the target COC.
36 | Don't mention avg conductivity say whether it the conductivity is within range as 100 %
37 | If the current COC is same as target COC within 20 % then mention that the water efficiency is good.
38 | If current COC less than target COC mention that there could be water loss in the system
39 | If the final day avg COC same as target COC then mention currently everything is maintained in range
40 | If the final day avg COCless than target COC then mention that this will be inspected in upcoming service viist.
41 | If the current COC hiher than target COC mention that the blowdown/makeup valve needs inspection
42 | If the final day avg COC greater than target COC then mention that this will be inspected in upcoming service viist.
43 | Product Efficiency as 5 th heading
44 | Mention whether trace product is 100% within range.
45 | Compare actual consumption and target consumptiuon, if both are same mention product efficiency is good.
46 | If not mention whether there is excess or less product consumption .
47 | If the consumption is less, check if there is prod LL alarm or decrease in prod or increase in cond or cond HHalarm. If so, prod LL mention that reasons after running Prod LL alarm.
48 | Proactive summary as 6Th heading
49 | Mention the no.of alarms genertaed that month
50 | Mention the alarm and mention the recommendation for it
51 | Insight
52 | Mention calc for water loss and prod efficiency if there water efficiency is not in range
53 | Mention regarding asset preservation if the corrosion rate is not good and calculate if there is only decrease in corrosion
54 | Performance Summary as 6th heading
55 | Mention all parameter with HH and LL limit along with % of range
56 | Charts trend
57 | If product efficiency is not good plot flow Vs prod
58 | Mention comment for the above graph
59 | If water efficiency is not good plot flow Vs cond
60 | Mention comment for the above graph
61 | If the corrosion rate is not good plot MS corrosion rate or Copper corrosion rate
62 | Mention comment for the above graph