BUCKMAN DIGITAL WATER

Monthly Cooling Water Performance Report

Flowserve US Raleigh NC (US)

Reporting Month: July 2026

| Customer / Site | System | Controller | Prepared For |
| --- | --- | --- | --- |
| Flowserve US Raleigh NC (US) | Cooling Tower | 84253F5EE1C9 | Monthly Performance Review |

This report summarises corrosion control, scale control, microbial control, water efficiency, product efficiency, and proactive system support for Flowserve US Raleigh NC (US), July 2026, using controller setpoints, telemetry KPIs, field data, and service note records.

| Prepared By | Prepared Date | Report Status |
| --- | --- | --- |
| Buckman Digital Water | 06 August 2026 | Draft |

Executive Summary

System Health Check

Corrosion Control

Status: Excellent

The average mild steel corrosion rate was 1.10 MPY against the target of within 3.0 MPY, and the average copper corrosion rate was 0.0250 MPY against the target of within 0.5 MPY. Both corrosion indicators were maintained within the required control targets for the July reporting period, supporting excellent asset preservation for the cooling water system.

Scale Control

Status: Acceptable

Traced Product was within the Controller Setpoint control range for 41.3% of the reporting month. Traced Product was higher than target during the initial part of the month and improved later, but end-of-month control was 52.4% within range, so it is not yet consistently maintained well.

Traced Product averaged 91.9 ppm against the SCC target range of 82.0-88.0 ppm. The product was higher than target during the initial part of the month and moved closer to the control band later, but end-of-month control was not yet consistently maintained well. Conductivity was below its SCC range for most of the same period, so water loss, dilution, or blowdown/makeup behavior should be inspected during the upcoming service visit.

Microbial Control

Status: Acceptable

FRC data was not available in the MDE data for this reporting period and will be checked during the upcoming service visit. ORP spike response after biocide feed was consistent, indicating the slug dosage of biocide is successful.

Dip-slide analysis was not available for this reporting period and will be measured during the upcoming service visit.

Water Efficiency

Makeup water conductivity is not available for this site. Actual cycles of concentration cannot be calculated. Makeup conductivity should be captured at the next service visit.

Conductivity averaged 890.6 uS/cm against the SCC range of 930-970 uS/cm, with 20.2% of July readings maintained within range. Makeup conductivity was not available, so current COC and target COC could not be calculated; this will be reviewed when makeup conductivity data is available. Because conductivity was below the control range for much of the period, possible water loss, makeup/blowdown behavior, or dilution should be inspected during the upcoming service visit.

Product Efficiency

Status: Acceptable

Traced Product was 41.3% within the SCC control range, and actual product consumption data was not available for direct comparison with target consumption. Product efficiency should be reviewed by checking calibration, feed settings, and pump operation, then comparing actual consumption once usage data is available.

Proactive System Support

No service notes were recorded for this reporting period. The main proactive follow-up items are to verify Traced Product feed and fluorometer calibration, review conductivity control and water balance, and collect FRC during the next service visit.

Performance Summary

Controller Setpoints are used as control limits below. % In Range is calculated from the full reporting month telemetry.

| Parameter | Context Point | Average | Std Dev | Min | Max | Lower Limit | Upper Limit | % In Range | Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Corrosion – MS (MPY) | ACM Skid | 1.102 | 0.688 | 0.247 | 2.818 | 0.00 | 3.00 | 100.0% | ✓ Excellent |
| Corrosion – Cu (MPY) | ACM Skid | 0.025 | 0.143 | 0.010 | 3.308 | 0.00 | 0.50 | 99.8% | ✓ Excellent |
| Traced Product (ppm) | ACM Skid | 91.921 | 10.177 | 78.792 | 274.838 | 82.0 | 88.0 | 41.3% | ⚠ Acceptable |
| Conductivity (µS/cm) | ACM Skid | 890.606 | 44.201 | 453.220 | 988.564 | 930 | 970 | 20.2% | ✗ Critical |
| pH | ACM Skid | 8.455 | 0.256 | 7.458 | 8.914 | 7.50 | 10.00 | 100.0% | ℹ Info |
| ORP (mV) | ACM Skid | 549.451 | 152.851 | 78.917 | 819.747 | – | – | – | See chart |
| Turbidity (NTU) | ACM Skid | 3.160 | 1.191 | 1.643 | 38.197 | – | 75.0 | – | ℹ Info |
| Cell Fouling (%) | ACM Skid | 15.129 | 3.677 | 10.370 | 23.008 | – | 30.0 | – | ℹ Info |
| FRC | Field Data | Not avail. | – | – | – | – | – | – | ⚠ Check |

Charts and Comments

Corrosion Rate

Figure 1: Corrosion Rate — July 2026

Comment: The corrosion trend remained controlled overall, with recent mild steel and copper readings staying comfortably within the required limits.

Traced Product Control Trend

Figure 2: Traced Product — July 2026

Comment: The Traced Product trend spent part of July within range but remained above the SCC control band often enough to require continued review.

ORP vs Copper Corrosion Rate

Figure 3: ORP vs Copper Corrosion Rate — July 2026

Comment: The ORP response showed treatment activity without requiring absolute ORP values to be reported in the narrative.

Oxidizing Biocide Pump Relay vs Copper Corrosion

Figure 4: Oxidizing Biocide Pump Relay vs Copper Corrosion — July 2026

Electrode Conductivity

Figure 5: Electrode Conductivity — July 2026

Comment: The conductivity trend was below the SCC range for much of the recent period but moved closer to the control band near the end of the month.

Closing Summary

Flowserve US Raleigh NC maintained good corrosion control during July 2026, while scale control and product efficiency should continue to be reviewed because Traced Product was above the SCC range for part of the month. Conductivity control requires attention due to low in-range performance, and FRC should be measured during the upcoming service visit to confirm microbial control.